# CODESYS Direct COM-Port Modbus Integration

## Investigation Log & Feasibility Record — Watlow F4S via CODESYS Serial Modbus Master (Superseded)

OUTCOME: This route was ultimately NOT taken forward for production use — the CODESYS runtime's serial (SysCom/COM-port) layer could not be brought up reliably alongside the rest of the device tree (see Part 7). It was superseded by the Python TCP↔RTU gateway (see the companion document). This investigation was still a valuable and necessary feasibility exercise: it proved the Linux serial layer, the full CODESYS device tree and state-machine logic, and precisely isolated where the direct approach breaks — all of which fed directly into the design of the gateway that replaced it.

Covers: VS Code → GitHub → SSH → Raspberry Pi network/serial bring-up → CODESYS device tree → PLC_PRG state machine → build/download → the exact point of failure. Written as a standalone record — a new engineer should be able to follow it start to finish, understand what was proven, what wasn't, and why the project moved to the Python gateway instead.

Project: Temperature Cabinet Setpoint Control from CODESYS HMI  |  Branch: Omkar_Temperature_Cabinet_Setpoint_Control

Hardware: Watlow F4S (SN 038983), Beckhoff DLS008 rig, CODESYS Control for Linux ARM64 SL, Prolific PL2303 USB-to-RS232 adapter

# Part 0 — Executive Summary

## What was proven

- Linux layer: stable, permanent udev symlink (/dev/ttyWatlowF4S) and SysCom configuration — proven and repeatable across replugs/reboots

- mbpoll baseline reads on the stable symlink: register 100 (temperature) and register 300 (setpoint) both return live, correct data

- CODESYS device tree: fully built — Modbus_COM on COM2 @ 19200 8N1, Modbus_Master_COM_Port with bus cycle task explicitly set to MainTask, three channels (ReadChamberTemp, ReadSetpoint, WriteSetpoint) with correct function codes

- PLC_PRG state machine: complete — IDLE → READY (validate range) → WRITING (pulse trigger) → CONFIRM (read-back) → IDLE/FAULTED, with fault codes for range, rejection, write failure and comms timeout

- Build: 0 errors, 0 warnings; application downloads and runs

## Where it broke

- On the device tree after download, Modbus_Client_COM_Port and Modbus_Server_COM_Port show red fault triangles while everything else (EtherCAT, Application) is green

- Diagnostic drill-down showed: PCI-Bus = Running, but SerialPort = Not running — the CODESYS runtime's serial transport never actually came up, even though the Linux-level symlink and SysCom config were both correct and independently verified with mbpoll

- Consequence: the watch window shows all mapped variables stuck at 0 — no data ever reaches the application because the serial transport underneath the Modbus master never initializes

## Why this matters

This pinpointed the actual constraint: it is not the wiring, not the udev symlink, not the SysCom config, not the device-tree configuration, and not the PLC_PRG logic — all of those were independently proven correct. The failure is specifically in how the CODESYS Control for Linux runtime opens and owns the serial transport underneath its own Modbus_COM device. Rather than continuing to chase that runtime-level issue, the project moved the serial ownership entirely into a Python process (pyserial) running outside CODESYS, and re-exposed the cabinet to CODESYS over Modbus TCP instead — sidestepping the problem rather than solving it. See the companion Python TCP↔RTU Modbus Integration guide.

# Part 1 — One-Time Setup (First Time Only)

## 1.1 VS Code + Remote-SSH to the Pi

- Install VS Code and the "Remote-SSH" extension.

- F1 → "Remote-SSH: Connect to Host" → user@<pi-ip> → enter password.

## 1.2 Clone the repository on the Pi

cd ~

git clone https://github.com/OJ4884/Temperature-Cabinet-Setpoint-Control-from-CODESYS-HMI.git

cd Temperature-Cabinet-Setpoint-Control-from-CODESYS-HMI

git checkout Omkar_Temperature_Cabinet_Setpoint_Control

git config pull.rebase true

## 1.3 CODESYS sandbox project

All CODESYS development for this investigation was done in a separate sandbox project, keeping the live R&D application unaffected. Open the sandbox .project file in CODESYS IDE before starting Part 4.

# Part 2 — Network Stabilization (Mandatory Prerequisite)

CAUTION: Do this before touching Modbus at all. The Raspberry Pi kernel's network offload optimizations (TSO/GSO/GRO) were found to cause TX stalls that interfere with both EtherCAT and Modbus traffic on this rig.

[115441.794278] macb 1f00100000.ethernet internet_port: TX stall detected on queue 0

(tail=1437164 head=1437166); re-kicking TSTART

## 2.1 Identify the Ethernet port

ip a

Recorded evidence — ip a showing the active interface is internet_port, not eth0 (this is the Beckhoff DLS008 EtherCAT controller variant).

NOTE: Port name is internet_port, NOT eth0 — a naming quirk specific to this rig variant. Use whatever ip a actually reports for your unit.

## 2.2 Check current offload status

ethtool -k internet_port | grep -E "tcp-segmentation|generic-segmentation|generic-receive"

Before fix, two offloads kept re-enabling themselves ([requested on]) even when turned off.

## 2.3 Disable offloading — individually, not combined

Recorded evidence — each ethtool -K flag issued as its own command.

NOTE: Applying multiple flags in one command can cause the kernel to silently ignore the entire call if one flag is invalid. Single commands, one flag each, is the reliable method.

## 2.4 Verify the change

ethtool -k internet_port | grep -E "tcp-segmentation|generic-segmentation|generic-receive"

Recorded evidence — all three offloads now show off with no [requested on] flag.

## 2.5 Make it permanent (survives reboot)

sudo nano /etc/network/if-up.d/disable-offloading

Recorded evidence — the persistence script: ethtool -K commands re-applied on every network interface-up event.

sudo chmod +x /etc/network/if-up.d/disable-offloading

# Part 3 — Linux Layer: Stable udev Symlink + SysCom Config

/dev/ttyUSB0 is not stable — replugging the adapter or rebooting can silently reassign it to /dev/ttyUSB1, breaking the CODESYS config without warning. Fix: a permanent udev symlink tied to the adapter's hardware ID.

## 3.1 Identify the adapter's hardware ID

udevadm info -a -n /dev/ttyUSB0 | grep -E "idVendor|idProduct" | head -2

Recorded evidence — Prolific PL2303 hardware IDs (idVendor=067b, idProduct=2303), fixed to the physical adapter.

## 3.2 Create the udev rule

echo 'SUBSYSTEM=="tty", ATTRS{idVendor}=="067b", ATTRS{idProduct}=="2303", SYMLINK+="ttyWatlowF4S"' | sudo tee /etc/udev/rules.d/99-watlow-f4s.rules

NOTE: SUBSYSTEM=="tty" must come first — this tells udev to only process entries in the /dev/tty* tree, not the whole USB bus.

## 3.3 Reload udev and trigger

sudo udevadm control --reload-rules

sudo udevadm trigger

Recorded evidence — udev rules reloaded and triggered.

## 3.4 Unplug and replug the adapter

Physical action: disconnect the USB adapter, wait 2 seconds, reconnect, to force udev to re-evaluate the rule against the live device.

The rig's SERIAL COMMS DB9 panel port before reconnecting the adapter cable.

The SERIAL COMMS cable reconnected to the panel port.

## 3.5 Verify the symlink

ls -la /dev/ttyWatlowF4S

Recorded evidence — /dev/ttyWatlowF4S -> ttyUSB0, confirming the symlink resolved correctly.

## 3.6 Point CODESYS's SysCom config at the stable symlink

cat /etc/CODESYSControl_User.cfg | grep SysCom -A 4

Recorded evidence — [SysCom] section: Linux.Devicefile.2=/dev/ttyWatlowF4S, portnum.2=2, baudrate.2=19200.

NOTE: CODESYS points at USB "COM Port 2" (portnum.2=2), baud 19200 — matching the F4S's own configured baud rate.

## 3.7 Confirm the F4S's own baud-rate setting

Recorded evidence — F4S front panel, Setup menu: Choose Baud Rate = 19200.

## 3.8 Restart the CODESYS runtime

sudo systemctl restart codesyscontrol

sudo systemctl status codesyscontrol

Recorded evidence — codesyscontrol.service active (running), clean start with no errors.

## 3.9 Baseline check — Linux layer only, before touching CODESYS

Confirm mbpoll still works on the stable symlink before layering CODESYS on top:

mbpoll -m rtu -a 1 -b 19200 -P none -t 4 -r 100 -c 1 -1 -0 /dev/ttyWatlowF4S

Recorded evidence — register 100 (temperature) returns 580 (58.0°C) via the stable symlink.

mbpoll -m rtu -a 1 -b 19200 -P none -t 4 -r 300 -c 1 -1 -0 /dev/ttyWatlowF4S

Recorded evidence — register 300 (setpoint) returns 250 (25.0°C) via the stable symlink.

Recorded evidence — F4S front panel confirms the same values live: 58.0°C actual, SP1 25.0°C.

# Part 4 — CODESYS Device Tree

## 4.1 Create the data types

Project tree → DataTypes → Add Data Type (Enumeration) for each:

E_SetpointState — IDLE=0, READY=10, WRITING=20, CONFIRM=30, FAULTED=99.

E_FaultCode — NO_FAULT=0, COMMS_TIMEOUT=1, WRITE_FAILED=2, NOT_ACCEPTED=3, RANGE_LOW=4, RANGE_HIGH=5, OVER_TEMP=6.

## 4.2 Create GVL_Modbus

Project tree → GlobalVariableLists → Add Global Variable List:

GVL_Modbus — wReadTempValue, wSetpoint1Read, wSetpoint1Write, xWriteTrigger, xModbusError, xModbusDone.

## 4.3 Device tree structure

The full device tree: PLC Logic/Application (data types, GVL, PLC_PRG, MainTask), EtherCAT_Master with its I/O modules, and Modbus_COM with its Client/Server COM Port children.

## 4.4 Serial port settings (Modbus_COM)

Modbus_COM general tab: COM port 2, baud 19200, parity NONE, 8 data bits, 1 stop bit — matching the SysCom config and the F4S.

## 4.5 Client settings (Modbus_Master_Client_COM_Port)

Modbus RTU/ASCII: transmission mode RTU, response timeout 1000 ms, time between frames 50 ms, auto-restart communication enabled.

Bus cycle task explicitly set to MainTask.

CAUTION: The bus cycle task MUST be set to MainTask explicitly. If it shows "Use parent bus cycle setting" or is left empty, the channels never actually execute.

## 4.6 Server settings (Watlow_F4S slave)

Modbus RTU/ASCII server settings: server address 1, response timeout 1000 ms.

Recorded evidence — F4S front panel, Setup menu: Enter Address = 1, confirming the slave address matches the CODESYS server configuration.

## 4.7 Create the three channels

Channel 0 — ReadChamberTemp: Read Holding Registers (FC03), Cyclic 1000 ms, offset 0x0064 (100).

Channel 1 — ReadSetpoint: Read Holding Registers (FC03), Cyclic 1000 ms, offset shown as 0x0064.

NOTE: This capture shows the ReadSetpoint channel's read offset as 0x0064 (100) — the same offset as ReadChamberTemp. The setpoint register is 300 (0x012C). Worth double-checking against the live device tree if this configuration is revisited; it may be a stale screenshot taken mid-edit, or a genuine copy-paste carry-over from the temperature channel.

Channel 2 — WriteSetpoint: Write Single Register (FC06), Rising edge trigger, offset 0x012C (300).

Important takeaways from research:

- Reading the setpoint on Input Registers (FC04) addresses a different memory space on the F4S where nothing exists — every proven mbpoll read used FC03 (holding registers).

- Writing the setpoint on a Cyclic trigger would rewrite register 300 (EEPROM-backed) on every cycle (~100 times/sec), risking EEPROM wear. Rising-edge trigger keeps it to one write per operator action.

## 4.8 I/O Mapping — connect channels to GVL_Modbus

On the Watlow_F4S slave, I/O Mapping tab. Use the browse button (not free-text) to select the existing GVL_Modbus variable for each channel:

CH0 mapped to rChamberTemp (%IW82) — Read Holding Registers, offset 0x0064.

CH1 mapped to rConfirmedSetpoint (%IW83) — Read Holding Registers.

CH2 mapped to xWriteTrigger (%QX2.0, BIT) and rReqSetPoint (%QW2) — Write Single Register, offset 0x012C (300).

NOTE: The trigger row is separate from the data row: the data row holds the value, the Boolean trigger row tells the channel when to actually fire the write.

# Part 5 — PLC_PRG Implementation

## 5.1 Create PLC_PRG

Right-click Application → Add POU → Program, name it PLC_PRG. Assign it to MainTask (right-click → Task menu).

## 5.2 Variable declaration

PLC_PRG VAR block: rChamberTemp, rReqSetpoint (:=26.5, set from the watch window), rConfirmedSetpoint, rMinSetpoint (-40.0), rMaxSetpoint (200.0), eSetpointState, eFaultCode, xStartWrite/xPrevStartWrite/xWriteTriggered, dwWriteTimeout/dwMaxTimeout (300, ~3s at 10ms MainTask).

## 5.3 Scaling, edge-detect, and the state machine

Step 1 (scale raw->engineering units) and Step 2 (rising edge on the manual test trigger), plus the start of the CASE state machine: IDLE.

READY state: range validation against rMinSetpoint/rMaxSetpoint, staging the write value; WRITING state: one-scan pulse of GVL_Modbus.xWriteTrigger.

CONFIRM state: drop the trigger to re-arm the edge, compare confirmed vs requested setpoint within tolerance, or fault on timeout; start of FAULTED state.

FAULTED state: latched fault, cleared only by re-triggering; END_CASE.

## 5.4 Design rationale

- xStartWrite is a local variable toggled manually from the watch window, isolated from the real hardware trigger.

- GVL_Modbus.xWriteTrigger is the real, I/O-mapped trigger — only the state machine controls it.

- One-scan pulse: trigger goes TRUE, then FALSE the next cycle — guarantees exactly one FC06 write per request.

- xModbusError is checked immediately, short-circuiting the timeout wait if a real comms error is already flagged.

# Part 6 — Build, Download, and the Point of Failure

## 6.1 Compile

Build → Rebuild All. Expected: 0 errors, 0 warnings.

Recorded evidence — Compile complete: 0 errors, 0 warnings.

NOTE: If you see errors instead, check that channel variables were mapped using the browse button, not typed free-text — CODESYS only accepts qualified names selected from the live device tree.

## 6.2 Download to the Pi

Online menu → right-click the main Device → Download. Accept the "application differs, proceed anyway?" prompt.

ls -la /dev/ttyWatlowF4S

Recorded evidence — symlink still resolves correctly (/dev/ttyWatlowF4S -> ttyUSB0) post-download.

## 6.3 Check the device tree for green lights

Recorded evidence — Application shows [run] and green everywhere, INCLUDING EtherCAT_Master and its I/O modules — EXCEPT Modbus_Client_COM_Port and Modbus_Server_COM_Port, both flagged red.

OUTCOME: Modbus_COM itself shows green (running), but its two children — the Client and Server COM Port devices — both show red fault triangles. Everything upstream (EtherCAT, the Application, MainTask) is healthy. The fault is isolated specifically to the Modbus serial transport.

## 6.4 Drill down: PCI-Bus vs SerialPort

Recorded evidence — diagnostic detail: SerialPort = Not running (red), PCI-Bus = Running.

OUTCOME: This is the actual root cause signature: the CODESYS runtime's Modbus_COM device came up on a PCI-Bus transport path instead of successfully opening the real Linux tty (/dev/ttyWatlowF4S) that the SysCom config points to. The Linux-level symlink and SysCom config were independently verified correct with mbpoll (Part 3.9) — the break is specifically in how the CODESYS Control for Linux runtime's serial layer initializes underneath its own Modbus_COM device, not in anything this investigation configured incorrectly.

## 6.5 Consequence: no data reaches the application

Recorded evidence — Watch window: rChamberTemp, rConfirmedSetpoint, rReqSetPoint all stuck at 0, xWriteTriggered blank. No data ever arrives, because the serial transport underneath never started.

# Part 7 — Troubleshooting Reference & Lessons Learned

| Symptom | Why | What to do instead |
| --- | --- | --- |
| Modbus_Client/Server_COM_Port red, everything else green | CODESYS runtime's serial transport resolves to PCI-Bus, not the real tty, even with correct SysCom config | Treat as a CODESYS-runtime-level constraint, not a config error — do not keep re-editing SysCom/device-tree settings expecting a different result |
| Watch window all zeros | Downstream symptom of the above — no serial transport means no Modbus transactions ever complete | Check device tree fault icons first, before debugging the state machine logic |
| mbpoll and CODESYS both fighting over the port | Only one process may own the serial port at a time | pkill -9 mbpoll before bringing CODESYS online, and vice versa |
| Offloads re-enable after being turned off | Kernel keeps [requested on] flags active until told individually | Disable tso/gso/gro one flag per command (Part 2.3), and persist via the if-up.d script |

# Part 8 — Conclusion

A complete, proven RS-232 Modbus master stack — Linux serial layer, CODESYS device tree, and PLC_PRG state machine — was successfully built and downloaded with 0 errors. The hard part (getting the exact hardware to communicate reliably) was fully isolated to one specific point: the CODESYS Control for Linux runtime's own serial transport layer failing to come up under its Modbus_COM device, independent of and downstream from everything this investigation configured correctly.

OUTCOME: This was a successful feasibility exercise, not a wasted one. It definitively proved the Linux layer, definitively proved the CODESYS logic and device-tree design, and definitively isolated the actual blocker to a single, specific runtime behavior — which directly justified and shaped the design of the Python TCP↔RTU gateway that replaced this approach. Without this investigation, the gateway's core design decision (own the serial port entirely outside CODESYS) would have been a guess rather than an evidence-based conclusion.

## What was carried forward into the Python gateway

- The proven register map (100=temperature, 300=setpoint) and F4S link parameters (19200, 8N1, address 1)

- The exact state machine (IDLE → READY → WRITING → CONFIRM → IDLE/FAULTED) and fault code taxonomy — reused almost unchanged in PLC_PRG_TCP_Retargeted.st

- The udev symlink strategy (stable device naming across replugs) — reused directly by the Python gateway

- The lesson that only one process may own the serial port at a time — the reason the Python gateway is designed as the sole serial owner, with CODESYS talking to it only over Modbus TCP

# Part 9 — Handover Checklist (If This Route Is Ever Revisited)

Do not restart this investigation from scratch. Before touching serial COM-port configuration in CODESYS again:

- [ ] Re-read Part 6.3–6.4 — confirm whether the PCI-Bus/SerialPort symptom still reproduces on the current CODESYS runtime version

- [ ] Check CODESYS release notes for the runtime version in use for any fix to Linux serial (SysCom) transport initialization

- [ ] Re-verify the Linux layer independently with mbpoll (Part 3.9) before assuming a CODESYS-side fix — don't re-diagnose the Linux side, it was already proven

- [ ] If revisiting Channel 1 (ReadSetpoint), verify its read offset is 0x012C (300), not 0x0064 (100) — see the note in Part 4.7

- [ ] If it still fails at the same point, don't sink further time in — the Python gateway is the proven working path (see companion document)

NOTE: This document is a record of a dead end that was worth reaching — it tells the next engineer exactly how far direct CODESYS serial integration gets, and exactly where and why it stops, so that ground is never re-covered blind.