# Python TCP↔RTU Modbus Integration

## Complete End-to-End Guide — CODESYS HMI to Watlow F4S via Raspberry Pi Gateway

OUTCOME: This route was successful and is the adopted solution. The gateway is proven end-to-end on real hardware: RTU reads, write-with-confirmation, and range-validation all pass (T1–T4), the Python process reliably owns the serial port and re-exposes the cabinet over Modbus TCP, and a written setpoint has been visually confirmed on the F4S front panel. It superseded the direct CODESYS-to-COM-port approach (see the companion CODESYS investigation log) by moving serial ownership out of the CODESYS runtime entirely — sidestepping the runtime-level serial fault found there. Remaining work is CODESYS-side integration only (Part 8), not the gateway itself.

Covers: VS Code → GitHub → SSH → Raspberry Pi → Python gateway → RTU/TCP read-write test → CODESYS. Written as a standalone handover document — a new engineer with no prior context should be able to follow it start to finish, including recovery when the USB adapter is unplugged and re-plugged mid-project.

Project: Temperature Cabinet Setpoint Control from CODESYS HMI  |  Branch: Omkar_Temperature_Cabinet_Setpoint_Control

Hardware: Watlow F4S temperature controller, Prolific/PL2303-class USB-to-RS232 adapter, Raspberry Pi (Debian)

# Part 0 — What This Is (Read This First)

CODESYS cannot talk RS-232/RTU directly in this setup, and the Watlow F4S cannot speak Modbus TCP. The Python gateway sits in the middle: it is the ONLY process allowed to touch the serial port, and it re-exposes the cabinet as a 5-register Modbus TCP slave that CODESYS talks to over the network.

CODESYS (TCP master)  --TCP:502-->  [Python gateway]  --RTU-->  Watlow F4S

### Register Map (Modbus TCP, unit id 1, all values ×10 integers)

| Reg | Name | Direction | Meaning |
| --- | --- | --- | --- |
| 0 | REG_REQ_SP | CODESYS → gateway | Requested setpoint, e.g. 265 = 26.5°C |
| 1 | REG_TRIGGER | CODESYS → gateway | Write 1 to apply; gateway clears to 0 when done |
| 2 | REG_TEMP | gateway → CODESYS | Current chamber temperature |
| 3 | REG_SP_READ | gateway → CODESYS | Confirmed setpoint (read back from F4S) |
| 4 | REG_STATUS | gateway → CODESYS | 0=OK 2=WRITE_FAILED 3=NOT_ACCEPTED 4=RANGE 5=COMMS |

NOTE: Valid setpoint range enforced by the gateway is −40 to 200 °C (raw −400 to 2000). F4S-side RTU registers used: 100 = temperature, 300 = setpoint, slave address 1, 19200 baud 8N1.

Files (all under codesys-python-tcp-integration/python-gateway/):

- f4s_gateway.py — the gateway itself (RTU cyclic thread + Modbus TCP server)

- test_rtu_write.py — TCP client script exercising read / write-confirm / range-reject

- requirements.txt — pinned dependencies (pymodbus==3.12.1 — do not bump, see Part 10)

- README.md — canonical reference this document is built from

# Part 1 — One-Time Setup (First Time Only)

Do this once per laptop / new engineer. If you've already got VS Code Remote-SSH working against the Pi, skip to Part 2.

## 1.1 Install VS Code and the Remote-SSH extension

- Install Visual Studio Code on your laptop.

- Install the "Remote - SSH" extension from the Extensions marketplace.

## 1.2 Get SSH access to the Raspberry Pi

- Confirm the Pi's IP address on your network (this guide uses 10.1.6.17 as the example throughout).

- In VS Code, press F1 → "Remote-SSH: Connect to Host" → enter user@10.1.6.17.

- Enter the SSH password when prompted. VS Code will install its remote server component on first connect — this takes a minute.

- Once connected, the bottom-left corner of VS Code shows "SSH: 10.1.6.17".

## 1.3 Clone the repository on the Pi

cd ~

git clone https://github.com/OJ4884/Temperature-Cabinet-Setpoint-Control-from-CODESYS-HMI.git

cd Temperature-Cabinet-Setpoint-Control-from-CODESYS-HMI

git checkout Omkar_Temperature_Cabinet_Setpoint_Control

## 1.4 Configure git for rebase-based pulls (avoids merge-commit clutter)

git config pull.rebase true

git config --global user.name "Your Name"

git config --global user.email "you@example.com"

## 1.5 Add your user to the dialout group (serial port access)

sudo usermod -a -G dialout $USER

NOTE: Log out and back in (or reboot the Pi) for the group change to take effect. Verify with: groups — you should see dialout listed.

## 1.6 Install Python dependencies

cd codesys-python-tcp-integration/python-gateway

pip3 install -r requirements.txt --break-system-packages

pip3 list | grep pymodbus   # must print 3.12.1 exactly

CAUTION: pymodbus MUST stay pinned at 3.12.1. Version 3.13+ silently breaks the gateway — TCP reads get stuck at 0 and writes never take effect. Full root-cause explanation is in Part 10, item 5. Never run pip install --upgrade pymodbus.

## 1.7 Confirm the serial adapter has a stable device name (udev rule)

The repo's udev rule maps the USB-to-RS232 adapter to a fixed symlink, /dev/ttyWatlowF4S, regardless of which /dev/ttyUSBx number the kernel assigns on a given plug-in. Confirm it exists:

ls -la /dev/ttyWatlowF4S

If missing, see linux-integration/README.md Part 1 for adapter bring-up and the udev rule setup — that is a one-time hardware step and is out of scope for this document.

# Part 2 — Daily Startup Runbook

Two starting conditions, depending on whether the USB-to-RS232 adapter is still plugged into the Pi from last time. Work through the one that matches reality.

## Condition A — Adapter Already Plugged In (Normal Day)

Use this when the adapter has been sitting in the Pi's USB port since the last session. The gateway runs as a systemd service, so it also survives Pi reboots on its own.

- Visually confirm the USB-to-RS232 adapter is still seated in the Pi and the DB9 wiring is still landed on the F4S terminal block (Tx white → 14, Rx red → 15, GND black → 16). No action needed if it looks fine.

- On your laptop: launch VS Code.

- File → Open Recent → pick the Remote-SSH workspace for the Pi's IP.

- Enter the SSH password when prompted; wait for VS Code to finish attaching.

- Open an integrated terminal (Ctrl+`) — you are now on the Pi.

- Sync the repo:

cd ~/Temperature-Cabinet-Setpoint-Control-from-CODESYS-HMI

git fetch origin Omkar_Temperature_Cabinet_Setpoint_Control

git pull origin Omkar_Temperature_Cabinet_Setpoint_Control

- Confirm the serial symlink is present:

ls -la /dev/ttyWatlowF4S

- Confirm the gateway service is already running:

sudo systemctl status f4s-gateway

sudo journalctl -u f4s-gateway -n 20

Look for active (running) and recent Temp: / SP: log lines. If it's not running: sudo systemctl start f4s-gateway, then re-check status.

- Run the full TCP verification (mbpoll one-liners or python3 test_rtu_write.py) — see Part 6.

- Visually confirm on the F4S front panel that the setpoint written in the previous step actually shows up.

- Only once all the above pass, move on to CODESYS Integration (Part 9).

# Part 3 — Adapter Was Unplugged (Full Re-Bring-Up)

Use this any time the adapter was physically removed — moved benches, someone unplugged it, new Pi, etc. This repeats the hardware bring-up before trusting the gateway again. Do not skip straight to starting the service.

- Plug the USB-to-RS232 adapter into the Pi.

- SSH in the same way as Condition A (VS Code → Open Recent → SSH → password → sync repo).

- Confirm the OS sees the adapter and note which device node it landed on:

dmesg | tail -n 20

# look for: usb ...: pl2303 converter now attached to ttyUSBx

- Confirm /dev/ttyWatlowF4S resolved to that node. The symlink is udev-rule-based, keyed on the adapter's USB ID, so it auto-attaches regardless of which ttyUSBx number the kernel assigns this time:

ls -la /dev/ttyWatlowF4S

CAUTION: If the symlink is missing or dangling, do not just point the gateway at /dev/ttyUSBx directly — fix the udev rule/symlink first so future replugs keep working unattended.

- Confirm dialout permissions are still correct:

./linux-integration/scripts/check-serial-permissions.sh /dev/ttyWatlowF4S

- Physically double-check the DB9 wiring is still seated at the F4S terminal block (Tx white → 14, Rx red → 15, GND black → 16) — reseating the adapter sometimes tugs the terminal block loose.

- Baseline the RTU link directly with mbpoll BEFORE trusting the gateway:

mbpoll -m rtu -a 1 -b 19200 -P none -t 4 -r 100 -c 1 -1 -0 /dev/ttyWatlowF4S

# expect a live temperature value matching the F4S front panel

- Restart the gateway service so it picks up the fresh serial connection immediately:

sudo systemctl restart f4s-gateway

sudo systemctl status f4s-gateway

- Continue from Condition A, step 8 onward — TCP verification → front panel confirmation → CODESYS.

# Part 4 — Adapter Re-Enumerates WHILE the Gateway Is Running

This is different from Part 3: the service was working fine, then the kernel silently reassigned the adapter (e.g. /dev/ttyUSB1 → /dev/ttyUSB0) with no wiring change. Symptom: clean Temp:/SP: logging suddenly turns into continuous [Errno 5] Input/output error followed by a permanent RTU comms timeout.

CAUTION: Do NOT start a second manual gateway process to "check" — it will open the new device node fine but fail to bind TCP port 502 because the stuck instance already holds it, leaving two competing processes.

Recovery — get back to exactly one instance, pointed at the current device node:

- Kill any manually-started python3 f4s_gateway.py (Ctrl+C in whichever terminal has one running in the foreground). Systemd is the only thing that should ever run this script.

- Restart the systemd instance so it reopens the serial port fresh:

sudo systemctl restart f4s-gateway

- Confirm the current device node and watch the logs come back clean:

ls -la /dev/ttyWatlowF4S

sudo journalctl -u f4s-gateway -n 20 -f

- Confirm clean Temp: / SP: lines with no Input/output error or comms timeout before doing anything else.

NOTE: Known gap: f4s_gateway.py does not auto-reconnect on I/O error. Until that is implemented, any adapter re-enumeration while the service is running requires this manual restart. Note it for the next engineer.

# Part 5 — Running the Gateway

## 5.1 Manual run (for testing/debugging)

Always navigate to the python-gateway folder first:

cd ~/Temperature-Cabinet-Setpoint-Control-from-CODESYS-HMI/codesys-python-tcp-integration/python-gateway

Port 502 needs root, or grant the bind capability once and run as a normal user (recommended):

# option 1: run as root

sudo python3 f4s_gateway.py

# option 2 (better): grant bind capability once, then run as your user

sudo setcap 'cap_net_bind_service=+ep' $(readlink -f $(which python3))

python3 f4s_gateway.py

Expected startup log:

=== F4S Gateway Starting ===

RTU connected: /dev/ttyWatlowF4S @ 19200

Cyclic task started (period=1.0s)

Starting TCP server on 0.0.0.0:502

TCP server ready on 0.0.0.0:502

Followed by Temp: NN.N°C / SP: NN.N°C debug lines every second — this confirms the RTU side is alive before you even touch TCP. Logs are written to ~/.f4s_gateway/f4s_gateway.log.

## 5.2 Permanent run (systemd) — recommended for normal operation

CAUTION: Do NOT set User=root in the service file. pip3 install --break-system-packages installs into YOUR user's site-packages, not root's. A service running as root will silently resolve a different, unpinned pymodbus install and fail with 'ModbusDeviceContext' object has no attribute 'getValues', even though everything worked when run manually. Grant the bind capability instead and run as your normal user.

sudo setcap 'cap_net_bind_service=+ep' $(readlink -f $(which python3))

sudo nano /etc/systemd/system/f4s-gateway.service

[Unit]

Description=F4S Modbus TCP<->RTU Gateway

After=network.target

[Service]

ExecStart=/usr/bin/python3 /path/to/.../codesys-python-tcp-integration/python-gateway/f4s_gateway.py

Restart=always

User=YOUR_USERNAME

WorkingDirectory=/path/to/.../codesys-python-tcp-integration/python-gateway

[Install]

WantedBy=multi-user.target

Replace /path/to/... with the actual clone path, and YOUR_USERNAME with the account that ran pip3 install -r requirements.txt (the same one already in the dialout group).

sudo systemctl daemon-reload

sudo systemctl enable --now f4s-gateway

sudo systemctl status f4s-gateway

Verify status and logs any time:

sudo systemctl status f4s-gateway

sudo journalctl -u f4s-gateway -f

# Part 6 — Verify the TCP Side (Do This Before Touching CODESYS)

From the gateway host or any machine on the network (replace 10.1.6.17 with the gateway's actual IP):

# read temperature (reg2)

mbpoll -m tcp -a 1 -t 4 -r 2 -c 1 -1 -0 10.1.6.17

# request 26.5C -> reg0 = 265, then apply -> reg1 = 1

mbpoll -m tcp -a 1 -t 4 -r 0 -0 10.1.6.17 265

mbpoll -m tcp -a 1 -t 4 -r 1 -0 10.1.6.17 1

# read back confirmed setpoint (reg3) and status (reg4)

mbpoll -m tcp -a 1 -t 4 -r 3 -c 1 -1 -0 10.1.6.17     # expect 265

mbpoll -m tcp -a 1 -t 4 -r 4 -c 1 -1 -0 10.1.6.17     # expect 0 (OK)

Or run the bundled test script, which does all of the above plus an out-of-range rejection test:

python3 test_rtu_write.py

CAUTION: The F4S must be on its main run page for a write to be accepted — same rule as for direct serial access. If it's in a menu, the write is silently rejected.

NOTE: If these all pass, the gateway is proven correct independent of CODESYS — any problem found after this point is in the CODESYS-side Modbus TCP master configuration, not the gateway.

# Part 7 — Full T1–T5 Test Plan

## Prerequisites

python3 --version              # 3.10+

pip3 install -r requirements.txt --break-system-packages

pip3 list | grep pymodbus       # expect 3.12.1

ls -la /dev/ttyWatlowF4S

mbpoll -m rtu -a 1 -b 19200 -P none -t 4 -r 100 -c 1 /dev/ttyWatlowF4S

mbpoll -m rtu -a 1 -b 19200 -P none -t 4 -r 300 -c 1 /dev/ttyWatlowF4S

## T1 — Gateway Startup & RTU Layer Verification

Terminal 1: cd into python-gateway and run python3 f4s_gateway.py. Terminal 2: tail -f ~/.f4s_gateway/f4s_gateway.log and confirm Temp:/SP: lines every second.

Pass criteria:

- RTU connected successfully

- Cyclic task started, TCP server listening on :502

- Logs show temperature/setpoint updates every 1s, no errors

## T2 — TCP Register Read (No Write)

With the gateway running, read all 5 holding registers from a Python client (address=0, count=5, device_id=1). Expect Reg[2] and Reg[3] to be non-zero and to match the F4S front panel; Reg[4] (status) = 0.

## T3 — TCP Register Write (Setpoint Trigger)

python3 test_rtu_write.py

Pass criteria:

- Write trigger accepted, trigger clears after processing

- Status = 0 (OK)

- Read-back shows new setpoint; log shows RTU write and confirmation

## T4 — Range Validation (Out-of-Range Write)

Write an out-of-range value (e.g. 250°C = 2500 raw, valid range is −40 to 200°C). Expect status = 4 (RANGE) and a log line: WARNING - Out of range: 250.0°C. F4S setpoint must remain unchanged.

## T5 — Communications Timeout (Optional, Advanced)

With the gateway running, physically disconnect the F4S serial cable, wait 5+ seconds, then read status — expect 5 (COMMS). Reconnect the cable and confirm recovery within ~1s with no crash.

# Part 8 — CODESYS Integration (After T1–T4 Pass)

## Step 1 — Add the Modbus TCP Master Device

- Devices → Add Device → search "Modbus" → select Modbus TCP Master.

- Configure: Network adapter = your LAN, IP address = gateway IP (e.g. 10.1.6.17), Port = 502, Slave ID = 1, Cycle time = 100 ms.

## Step 2 — Configure 5 TCP Channels

| Channel | Name | FC | Address | Length | Type | R/W |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | ReadTemp | 03 | 2 | 1 | WORD | Read |
| 2 | ReadSetpoint | 03 | 3 | 1 | WORD | Read |
| 3 | ReadStatus | 03 | 4 | 1 | WORD | Read |
| 4 | WriteSetpoint | 06 | 0 | 1 | WORD | Write |
| 5 | WriteTrigger | 06 | 1 | 1 | WORD | Write (RISING_EDGE) |

## Step 3 — Map Channels to GVL_Modbus (I/O Mapping)

- ReadTemp (reg 2) → GVL_Modbus.wInput1Value

- ReadSetpoint (reg 3) → GVL_Modbus.wSetpoint1Read

- ReadStatus (reg 4) → GVL_Modbus.wStatus

- WriteSetpoint (reg 0) → GVL_Modbus.wSetpoint1Write

- WriteTrigger (reg 1) → GVL_Modbus.xWriteTrigger

## Step 4 — Swap in the TCP-Retargeted PLC_PRG

Replace the serial PLC_PRG with PLC_PRG_TCP_Retargeted.st (same state machine — IDLE → READY → WRITING → CONFIRM → IDLE/FAULTED — but sourced from TCP channels instead of serial). Ensure E_SetpointState.dut and E_FaultCode.dut from src/DUTs/ are present in the project.

## Step 5 — Build, Download, Watch

Build (Ctrl+Shift+B), download to the sandbox PLC, start the task, and add GVL_Modbus.wInput1Value, wSetpoint1Read, and wStatus to a Watch Window. Confirm live updates every cycle and wStatus = 0.

## Step 6 — Manual Trigger Test

Set GVL_HMI.rReqSetpoint to a new value, pulse GVL_HMI.xSetBtn to TRUE, and confirm wSetpoint1Read updates to match and the F4S front panel shows the new setpoint within 1–2 seconds.

# Part 9 — Troubleshooting Reference

## 9.1 Serial / RTU layer (from linux-integration bring-up)

| Symptom | Likely Cause | Fix |
| --- | --- | --- |
| Read timeout | Parity mismatch, permissions, or wiring | Use -P none; confirm dialout group; re-check TX/RX/GND wiring |
| Off-by-one register value | 0-based vs 1-based addressing | Always pass the -0 flag to mbpoll |
| Write "succeeds" but read-back unchanged | F4S in menu/edit mode (most common) | Press ESCAPE on F4S until main run page shows, retry |
| Write timeout | Cable unplugged mid-write | Check dmesg for adapter disconnect, reseat cable |

## 9.2 Gateway-specific issues

| Symptom | Root Cause | Fix |
| --- | --- | --- |
| TCP reads always 0.0°C, trigger never clears | pymodbus 3.13+ deepcopies the datastore once at construction; RTU-thread writes never reach live TCP storage | Pin pymodbus==3.12.1 (requirements.txt) |
| AttributeError: ModbusDeviceContext has no attribute getValues — only under systemd | User=root in the service file resolves a different, unpinned pymodbus install than the one pip installed for your user | Never use User=root; setcap + run as your normal user |
| Stuck permanent RTU comms timeout, no wiring change | USB adapter re-enumerated (ttyUSB1→ttyUSB0); gateway never reopens the port | Kill manual instances, sudo systemctl restart f4s-gateway (see Part 4) |
| [Errno 98] address already in use on :502 | Two gateway processes running at once (manual + systemd) | Kill the manual one; only systemd should run the script |

NOTE: Full narrative root-cause writeups (including the pymodbus source-code walkthrough and off-by-one addressing bug) live in codesys-python-tcp-integration/python-gateway/README.md, Troubleshooting History section — read that if a fix here doesn't resolve it.

# Part 10 — Quick Command Reference

# Sync repo

git fetch origin Omkar_Temperature_Cabinet_Setpoint_Control && git pull origin Omkar_Temperature_Cabinet_Setpoint_Control

# Check adapter + symlink

dmesg | tail -20   &&   ls -la /dev/ttyWatlowF4S

# Gateway service

sudo systemctl status f4s-gateway

sudo systemctl restart f4s-gateway

sudo journalctl -u f4s-gateway -f

# TCP verification

python3 test_rtu_write.py

mbpoll -m tcp -a 1 -t 4 -r 2 -c 1 -1 -0 10.1.6.17    # read temp

mbpoll -m tcp -a 1 -t 4 -r 4 -c 1 -1 -0 10.1.6.17    # read status

# Part 11 — Handover Checklist

Give this to a new engineer taking over the cabinet. Work top to bottom; do not skip ahead.

- [ ] VS Code Remote-SSH connects to the Pi (Part 1.1–1.2)

- [ ] Repo cloned, on branch Omkar_Temperature_Cabinet_Setpoint_Control, pull.rebase=true set (Part 1.3–1.4)

- [ ] Your user is in the dialout group (Part 1.5)

- [ ] pip3 list shows pymodbus 3.12.1 exactly — not upgraded (Part 1.6)

- [ ] /dev/ttyWatlowF4S symlink resolves (Part 1.7)

- [ ] Ran Daily Startup Runbook Condition A or B as appropriate (Part 2–3)

- [ ] f4s-gateway systemd service is active (running), not User=root (Part 5.2)

- [ ] T1–T4 all pass (Part 7)

- [ ] F4S front panel confirms a written setpoint visually

- [ ] CODESYS Modbus TCP Master device configured and channels mapped (Part 8)

- [ ] Know the Part 4 recovery procedure by heart before leaving the adapter unattended

NOTE: If every box above is checked, the system is proven end-to-end and safe to hand over. If any box fails, stop and resolve it using the matching Part before proceeding — do not attempt CODESYS integration on an unproven gateway.

OUTCOME: Overall outcome: successful. This is the first approach in the investigation history (Linux bench test → CODESYS direct COM port → Python gateway) that closes the loop completely — proven read, write, confirmation, and fault reporting, all reachable from CODESYS over the network instead of a runtime-fragile serial link. It is the recommended path forward for this cabinet.